Company Name Here

Address

Address

Address

Address

Fire Risk Assessment

Date: 00th Month 20**

Created by

MB Health and Safety Ltd

Unit 1 Hedley Avenue, Grays Essex RM20 4EL

REGULATORY REFORM (FIRE SAFETY) ORDER 2005

FIRE RISK ASSESSMENT

| Responsible person (e.g. employer or person having control of the premises): | Company name here |
| --- | --- |
| Address of premises: | Company address here |
| Person(s) consulted: | Persons consulted with |
| Assessor: | Advisor name (MB Health & Safety Ltd) |
| Date of fire risk assessment: | 00th Month 20** |
| Date of previous fire risk assessment: | 00th Month 20** |
| Suggested date for review1 | On completion of actions and at least annually |
| The purpose of this report is to provide an assessment of the risk to life from fire in the premises, and, where appropriate, to make recommendations to ensure compliance with fire safety legislation. The report does not address the risk to property or business continuity from fire. |  |
| (Review No. 1 ) |  |

1 This fire risk assessment should be reviewed by a competent person by the date indicated above or at such earlier time as there is reason to suspect that it is no longer valid, or if there has been a significant change in the matters to which it relates, or if a fire occurs

The Assessment was undertaken in accordance with the general risk assessment principles set out in The Regulatory Reform (Fire Safety) Order 2005 in order to identify hazards that could contribute to injury of persons working in or resorting to the building.

There are five aspects that our Advisor has used their professional judgement to consider:

Identification of hazards

Assessment of those at risk

Evaluation of the risk

Methods of control

Further controls that are necessary

It is important that you study this fire risk assessment and understand its contents.

The fire risk assessment includes an Action Plan, which sets out the measures it is considered necessary for you to take to satisfy the requirements of the Fire Safety Order and to protect relevant persons (as defined in the Order) from fire. It is particularly important that you study the Action Plan.

If any recommendation in the Action Plan is unclear you should request further advice

The report does not address the risk to property or business continuity from fire.

More generally, this fire risk assessment forms only a foundation for management of fire safety in your premises and compliance with the Fire Safety Order. It is strongly recommended that you obtain a copy of the Fire Safety Order (http://www.legislation.gov.uk/uksi/2005/1541/contents/made) and relevant HM Government Guidance document(s) (https://www.gov.uk/workplace-fire-safety-your-responsibilities/fire-safety-advice-documents) applicable to your company.

GENERAL INFORMATION

| 1. | THE PREMISES |  |  |  |
| --- | --- | --- | --- | --- |
| 1.1 | Number of floors: 1 |  |  |  |
| 1.2 | Approximate floor area: |  |  |  |
|  |  | 0,000 m2 per floor |  |  |
|  |  | 0,000 m2 gross |  |  |
|  |  | m2 on ground floor |  |  |
| (delete units as appropriate) |  |  |  |  |
| 1.3 | Brief details of construction: |  |  |  |
|  | The property is of traditional brick and block with a pitched, tiled roof. |  |  |  |
| 1.4 | Use of premises: |  |  |  |
|  | Describe use here |  |  |  |
| 2. | THE OCCUPANTS |  |  |  |
| 2.1 | Approximate maximum number: >000 |  |  |  |
| 2.2 | Approximate number of employees at any one time: >000 |  |  |  |
| 2.3 | Maximum number of members of public at any one time: >000 |  |  |  |
| 3. | OCCUPANTS ESPECIALLY AT RISK FROM FIRE |  |  |  |
| 3.1 | Sleeping occupants: None |  |  |  |
| 3.2 | Disabled occupants: None |  |  |  |
| 3.3 | Occupants in remote areas and lone workers: Lone workers - staff and overnight security personnel |  |  |  |
| 3.4 | Young person’s: None |  |  |  |
| 3.5 | Others: Ad-hoc Visitors and Contractors |  |  |  |
|  | Comments: |  |  |  |
| 4. | FIRE LOSS EXPERIENCE |  |  |  |
|  | There is no reported Fire loss history. |  |  |  |
| 5. | OTHER RELEVANT INFORMATION |  |  |  |
|  | This risk assessment covers the property as required by the Regulatory Reform Order (Fire Safety) 2005. All information contained within this report was obtained by the assessor from a visual inspection and a representative of the client. |  |  |  |

| 6. | RELEVANT FIRE SAFETY LEGISLATION |
| --- | --- |
| 6.1 | The following fire safety legislation applies to these premises: |
|  | The Regulatory Reform (Fire Safety) Order 2005 |
| 6.2 | The above legislation is enforced by: |
|  | Local Fire & Rescue Authority, HSE, Local Authority |
| 6.3 | Other legislation that makes significant requirements for fire precautions in these premises (other than the Building Regulations 2000): |
|  | None |
| 6.4 | Legislation to which 6.3 makes reference is enforced by: |
|  | Not applicable |
|  | Comments: |

FIRE HAZARDS AND THEIR ELIMINATION OR CONTROL

| 7. | ELECTRICAL SOURCES OF IGNITION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 7.1 | Reasonable measures taken to prevent fires of electrical origin? |  |  | Yes |  | No |  |
| 7.2 | More specifically: |  |  |  |  |  |  |
|  | Fixed installation periodically inspected and tested? |  |  | Yes |  | No |  |
|  | Portable appliance testing carried out? |  |  | Yes |  | No |  |
|  | Suitable policy regarding the use of personal electrical appliances? |  |  | Yes |  | No |  |
|  | Suitable limitation of trailing leads and adapters? |  |  | Yes |  | No |  |
|  | Comments and hazards observed: |  |  |  |  |  |  |
|  | - A fixed electrical condition report with a ‘Satisfactory’ rating was completed on 00 Month 20**. - PAT last completed December 2017. - All fixed electrical installations within the premises should be inspected every 5 years in accordance with The Electricity at Work Regulations / IET Wiring Regulations 18th Edition / British Standard 7671. It is recommended that the RP create a management action to ensure the electrical installation is retested in 20** and then five yearly thereafter. - Extension leads may constitute a tripping hazard and their use should be kept to a minimum. Extension leads and socket outlets should not be overloaded, and reel-type extension leads should be fully unwound if the appliance that they supply is of a wattage that is greater than that which may be used with an unwound lead. - Where cables and leads could constitute a tripping hazard their routes should be indicated with hazard warning tape, and where they may suffer damage by being walked upon they should be run in protective flexible plastic sheathing. - Regular inspection of such equipment is a requirement of the Electricity at Work Regulations 1989. Check the condition of all the cables and check that the appliances are fitted with correctly rated fuses; a fuse of too high a rating can lead to a fire in the appliance that it is supposed to protect. |  |  |  |  |  |  |
| 8. | SMOKING |  |  |  |  |  |  |
| 8.1 | Reasonable measures taken to prevent fires as a result of smoking? |  |  | Yes |  | No |  |
| 8.2 | More specifically: |  |  |  |  |  |  |
|  | Smoking prohibited in the building? |  |  | Yes |  | No |  |
|  | Smoking prohibited in appropriate areas? | N/A |  | Yes |  | No |  |
|  | Suitable arrangements for those who wish to smoke? |  |  | Yes |  | No |  |
|  | This policy appeared to be observed at time of inspection? |  |  | Yes |  | No |  |
|  | Comments and hazards observed: |  |  |  |  |  |  |
|  | - No evidence of illicit smoking was found in the premises at the time of this assessment. - Smoking is only permitted off site. - Suitable ‘No smoking’ signage is installed. |  |  |  |  |  |  |

| 9. | ARSON |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 9.1 | Does basic security against arson by outsiders appear reasonable?2 | Yes |  | No |  |
| 9.2 | Is there an absence of unnecessary fire load in close proximity to the premises or available for ignition by outsiders? | Yes |  | No |  |
|  | Comments and hazards observed: - A comprehensive CCTV system covers the main working areas. - Waste/baled materials are stored a sufficient distance from the main entrance gate. The gate is locked and secure when the site is unoccupied. - Building security is good. The premises is secured with a Yale type lock and a door entry system. - The building perimeter was clear of any fire load at the time of this assessment. - Arson is a major cause of fires in industry and commerce. Good security is probably the best protection against arson and therefore it is important to ensure that all means of access to the premises doors and windows are locked at all times when the building is unoccupied. |  |  |  |  |

2 Reasonable only in the context of this fire risk assessment. If specific advice on security (including security against arson) is required, the advice of a security specialist should be obtained.

| 10. | PORTABLE HEATERS AND HEATING INSTALLATIONS |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 10.1 | Is the use of portable heaters avoided as far as practicable? |  |  |  | Yes |  |  |  | No |  |  |
| 10.2 | If portable heaters are used: |  |  |  |  |  |  |  |  |  |  |
|  | Is the use of the more hazardous type (e.g. radiant bar fires or lpg appliances) avoided? |  | N/A |  | Yes |  |  |  | No |  |  |
|  | Are suitable measures taken to minimise the hazard of ignition of combustible materials? |  | N/A |  | Yes |  |  |  | No |  |  |
| 10.3 | Are fixed heating installations subject to regular maintenance? |  | N/A |  | Yes |  |  |  | No |  |  |
|  | Comments and hazards observed: - A Central heating system is installed. The central heating boiler is located with the ‘Break-out’ area. - Heating system (gas boiler(s)) subject to on-going maintenance programme by appointed Gas Safe contractor. - If portable heaters are used they must only ever be plugged directly into the mains supply and never via extension leads, trail leads or multi-gang plugs. |  |  |  |  |  |  |  |  |  |  |
| 11. | COOKING |  |  |  |  |  |  |  |  |  |  |
| 11.1 | Are reasonable measures taken to prevent fires as a result of cooking? | N/A |  |  | Yes |  |  |  | No |  |  |
| 11.2 | More specifically: |  |  |  |  |  |  |  |  |  |  |
|  | Filters changed and ductwork cleaned regularly? | N/A |  |  | Yes |  |  |  | No |  |  |
|  | Suitable extinguishing appliances available? |  |  |  | Yes |  |  |  | No |  |  |
|  | Comments and hazards observed: |  |  |  |  |  |  |  |  |  |  |
|  | No commercial cooking takes places on the premises. There is a domestic style kitchen located within each floor of the premises, each contains a microwave oven, fridge, kettle and a toaster. |  |  |  |  |  |  |  |  |  |  |
| 12. | LIGHTNING |  |  |  |  |  |  |  |  |  |  |
| 12.1 | Does the building have a lightning protection system? |  |  |  |  | Yes |  |  |  | No |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |  |  |  |  |
|  | No form of recognised earthing spike was apparent at the time of this assessment. |  |  |  |  |  |  |  |  |  |  |

| 13. | HOUSEKEEPING |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 13.1 | Is the standard of housekeeping adequate? |  |  |  |  | Yes |  |  |  | No |  |  |  |
| 13.2 | More specifically: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Combustible materials appear to be separated from ignition sources? |  |  |  |  | Yes |  |  |  | No |  |  |  |
|  | Avoidance of unnecessary accumulation of combustible materials or waste? |  |  |  |  | Yes |  |  |  | No |  |  |  |
|  | Appropriate storage of hazardous materials? |  | N/A |  |  | Yes |  |  |  | No |  |  |  |
|  | Avoidance of inappropriate storage of combustible materials? |  |  |  |  | Yes |  |  |  | No |  |  |  |
|  | Comments and hazards observed: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Housekeeping within the premises was found to be satisfactory at the time of this assessment. Care must be taken to avoid obstructing or blocking fire exit routes, and these areas must be monitored at all times by all staff. - A considerable amount of paperwork/fabric (inspiration boards) can be displayed throughout the building in corridors, rooms etc. There appeared to be no obvious risk at the time of the assessment, however, the company must monitor this to minimise the hazard of ignition of combustible materials. - All waste materials are regularly cleared from common areas of the property (internal and external). - Waste is well managed with waste stored in paladin style bins located at the rear of the premises. There is evidence of regular collections. - Some of the under stair areas off the lower ground floor are housing readily flammable materials. Most of the cupboards appear to have been suitably fire stopped. Recommend that: 1) Housekeeping be maintained to a high standard; 2) Any unnecessary materials be cleared; 3) The doors to the cupboards be KEPT LOCKED SHUT. |  |  |  |  |  |  |  |  |  |  |  |  |
| 14. | HAZARDS INTRODUCED BY OUTSIDE CONTRACTORS AND BUILDING WORKS |  |  |  |  |  |  |  |  |  |  |  |  |
| 14.1 | Are fire safety conditions imposed on outside contractors? |  |  |  |  | Yes |  |  |  | No |  |  |  |
| 14.2 | Is there satisfactory control over works carried out in the building by outside contractors (including “hot work” permits)? |  |  |  |  | Yes |  |  |  | No |  |  |  |
| 14.3 | If there are in-house maintenance personnel, are suitable precautions taken during “hot work,” including use of hot work permits? |  | N/A |  |  | Yes |  |  |  | No |  |  |  |
|  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - The company must ensure that sub-contracted maintenance personnel utilise a permit to work system in situations of high hazard/risk, for example, where there is a need to compromise existing fire precautions or when carrying out ‘hot works’. - Where appropriate, contractors employed by the RP must supply risk assessments and method statements prior to working. - It is recommended that the client give all contractors induction training prior to commencing work, which should include emergency procedures. - Additionally, the RP should arrange to conduct a post work inspection of the work area to ensure all works have been completed satisfactorily and safely, with no residual hazards present that could compromise the fire safety of the premises. |  |  |  |  |  |  |  |  |  |  |  |  |
| 15. | DANGEROUS SUBSTANCES |  |  |  |  |  |  |  |  |  |  |  |  |
| 15.1 | If dangerous substances are, or could be, used, has a risk assessment been carried out, as required by the Dangerous Substances and Explosive Atmospheres Regulations 2002? | N/A |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Comments: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | This risk assessment only considers the impact of the use or storage of dangerous substances to the extent necessary to determine the adequacy of the general fire precautions required under the Order to ensure the safety of relevant persons in the event of fire. |  |  |  |  |  |  |  |  |  |  |  |  |
| 16. | OTHER SIGNIFICANT FIRE HAZARDS THAT WARRANT CONSIDERATION INCLUDING PROCESS HAZARDS THAT IMPACT ON GENERAL FIRE PRECAUTIONS |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.1 | Hazards: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | None identified during this assessment, IT server equipment, Lighting. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - The cupboard housing the IT server equipment is used for the storage of stationary. This provides both a source of fuel and ignition in the same area. Providing a good standard of housekeeping is maintained no significant risk exists. Air conditioning is installed and ensures that the room does not get excessively hot in summer months. - Any fitted lighting within storage cupboards etc. should be low wattage, and preferably in a protective lamp housing. |  |  |  |  |  |  |  |  |  |  |  |  |
| 17. | MEANS OF ESCAPE FROM FIRE |  |  |  |  |  |  |  |  |  |  |  |  |
| 17.1 | It is considered that the building is provided with reasonable means of escape in case of fire. |  |  |  |  |  | Yes |  |  |  | No |  |  |
| 17.2 | More specifically: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Adequate design of escape routes? |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Adequate provision of exits? |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Exits easily and immediately openable where necessary? |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Fire exits open in direction of escape where necessary? |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Avoidance of sliding or revolving doors as fire exits where necessary? |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Satisfactory means for securing exits? |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Reasonable distances of travel: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Where there is a single direction of travel? |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | - Where there are alternative means of escape? |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Suitable protection of escape routes? |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Suitable fire precautions for all inner rooms? |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Escape routes unobstructed? |  |  |  |  |  | Yes |  |  |  | No |  |  |
| 17.3 | It is considered that the building is provided with reasonable arrangements for means of escape for disabled people. |  |  |  |  |  | Yes |  |  |  | No |  |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Final escape doors are fitted with ‘thumb turn’ locks. - The distances of travel are adequate and consistent with the guidance detailed in the HM Government Guide ‘Fire Risk Assessment – offices and shops’. Travel distances cannot practicably be reduced. - Escape signage provides clear, unambiguous information to enable people to safely leave the building in an emergency. - All floorings and stairways are in good visual condition. - There were no disabled occupants identified during this assessment. In the event of a disabled person requiring access to the premises (i.e. an employee, a visitor or a contractor) a Personal Emergency Evacuation Plan (PEEP) should be written and implemented by the Responsible Person. |  |  |  |  |  |  |  |  |  |  |  |  |
| Standard Advice: A place of safety is a place beyond the building in which a person is no longer in danger from fire. The designated place of safety must not be a dead-end situation from which people are unable to move further away from the building. Gangways and escape routes must never be obstructed. Obstructions such as unwanted furniture, unattended tea trolleys, coat racks, stocks of stationery, cleaning equipment, newly delivered goods, or goods awaiting collection all reduce the available width of escape routes and make it more difficult to evacuate people sufficiently quickly in the event of fire. Sources of heat or electrical equipment such as portable heaters, automatic vending machines, photocopiers etc. must never be sited on escape routes. Changes of level, electrical extension leads, unstuck flooring tiles, and small items - such as empty drink cans or contractors tools left on the floor are all capable of causing people to trip. Changes of level should be highlighted (e.g. by use of warning tape) and sufficiently illuminated. Wet floors and loose mats or runners constitute slipping hazards. Loose handrails, raised or loose floor tiles, and damaged nosing’s on steps may all cause people to trip whilst escaping from fire; on a staircase this could have disastrous consequences. Final exit doors must always remain unlocked whenever the premises are in use. If, for reasons of security, final exit doors have to be locked shut when the premises are not in use they may be secured by means that do not require the use of a key in order to release the door. Break-glass bolts (Redlam bolts), which are released by breaking a glass tube with a small hammer, are an acceptable way of keeping a fire exit door securely shut, provided that clear instructions as to how to release the bolt are displayed on or adjacent to the door and that a suitable hammer is attached by a chain that is anchored on or adjacent to the door. The ideal fastening for a fire exit door is a panic latch or lock that may be released by pressure upon a bar that runs across the full width of the door. Normally, doors on escape routes should open in the direction of travel. They must do so if they lead from an area from which more than 60 people may be required to escape, or if they lead from an area of high fire risk such as, for example, a kitchen. Disabled employees may require additional assistance to escape in the event of fire. A plan of how best they may be helped should be drawn up, and tested in the course of the regular fire drills. - Are lightweight evacuation chairs available? - Has each disabled person a personal "buddy" who is assigned to stay with them throughout the evacuation? - Is the building equipped with evacuation lifts that may be used by people in wheelchairs in the event of fire? - Are there ramps in place at all changes of level on escape routes? - Does the fire alarm system give a visual warning of fire for those who are profoundly deaf? - As an aid to those who are blind, are there tactile thresholds at the top and bottom of each flight of stairs? |  |  |  |  |  |  |  |  |  |  |  |  |  |

| 18. | MEASURES TO LIMIT FIRE SPREAD AND DEVELOPMENT |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 18.1 | It is considered that there is: |  |  |  |  |  |  |  |  |
|  | Compartmentation of a reasonable standard3 |  |  |  | Yes |  |  | No |  |
|  | Reasonable limitation of linings that might promote fire spread |  |  |  | Yes |  |  | No |  |
| 18.2 | As far as can reasonably be ascertained, fire dampers are provided as necessary to protect critical means of escape against passage of fire, smoke and combustion products in the early stages of the fire?4 | N/A |  |  | Yes |  |  | No |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |  |  |
|  | - A considerable amount of paperwork/fabric (inspiration boards) can be displayed throughout the building in corridors, rooms etc. There appeared to be no obvious risk at the time of the assessment, however, the company must monitor this to minimise the hazard of ignition of combustible materials. - From a brief sample inspection conducted during the course of this assessment, standards of compartmentation and fire stopping appeared to be adequate. - Fire doors were found to be in good visual condition and all found to be functioning correctly. Care must be taken to ensure fire doors are not wedged open and this should be monitored by all staff at all times. - All fire stopping materials and devices must be maintained in good order at all times. |  |  |  |  |  |  |  |  |
| Standard Advice: The principle structural means for limiting the spread of fire is compartmentation - dividing the building into compartments that are separated from each other by fire resistant walls and doors. The integrity of the compartmentation will be compromised if the fire doors have been badly hung, or if the compartmentation does not extend into the floor and ceiling voids that are created by suspended floors and ceilings. Penetration of fire walls by ducting or building services greatly reduces the effectiveness of the wall unless the spaces between the ducting or services and the hole through which they pass are completely filled with fire-resistant stopping. As with the use of wedges, fire extinguishers, or door stops to hold fire doors open, faulty self-closing devices or, those in which the tension has been incorrectly set, will not automatically close fire doors. This will put lives at risk in the event of fire. Employees should be made aware of the importance of reporting any self-closing devices that are not operating correctly. |  |  |  |  |  |  |  |  |  |
| 19. | EMERGENCY ESCAPE LIGHTING |  |  |  |  |  |  |  |  |
| 19.1 | Reasonable standard of emergency escape lighting system provided?5 |  |  |  | Yes |  |  | No |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |  |  |
|  | Based on visual inspection, but no test of illuminance levels or verification of full compliance with relevant British Standards carried out. |  |  |  |  |  |  |  |  |
| 20. | FIRE SAFETY SIGNS AND NOTICES |  |  |  |  |  |  |  |  |
| 20.1 | Reasonable standard of fire safety signs and notices? |  |  |  | Yes |  |  | No |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |  |  |
|  | - Escape signage provides clear, unambiguous information to enable people to safely leave the building in an emergency. - Fire instructions notices (‘Fire action’) are displayed on escape routes adjacent to fire break-glass call points and where staff frequently assemble in the premises, e.g. the ‘break-out’ area. - A notice with the words ‘Fire escape – keep clear’ is permanently displayed at about eye level on the external face of all doors which are provided as a means of escape in case of fire and which, because they are not normally used, may become obstructed. |  |  |  |  |  |  |  |  |
| 21. | MEANS OF GIVING WARNING IN CASE OF FIRE |  |  |  |  |  |  |  |  |
| 21.1 | Reasonable manually operated electrical fire alarm system provided?6 | Yes |  |  | Yes |  |  | No |  |
|  | (throughout Building) |  |  |  | (part of building only) |  |  |  |  |
| 21.2 | Automatic fire detection provided? | Yes |  |  | Yes |  |  | No |  |
|  | (throughout Building) |  |  |  | (part of building only) |  |  |  |  |
| 21.3 | Extent of automatic fire detection generally appropriate for the occupancy and fire risk? | N/A |  |  | Yes |  |  | No |  |
| 21.4 | Remote transmission of alarm signals? |  |  |  | Yes |  |  | No |  |
|  | Comments and deficiencies observed: There is an automatic fire alarm system installed throughout the whole premises, which from a visual inspection appears to conform to BS5839 Part 1 (L2). This is appropriate for this premises and proportionate to the risk. The inspection and testing of the fire alarm system is undertaken by an approved contractor appointed by the RP. |  |  |  |  |  |  |  |  |
| Standard Advice: By providing the earliest possible warning of fire, a properly installed and maintained automatic fire detection and alarm system does much to reduce the risk to life and property in the event of fire. The correct operation of a properly maintained system will greatly reduce the incidence of false alarms and, consequently, the incidence of unnecessary calls to the fire service. Raising the alarm should ideally be done automatically (If not it should be done from a place of safety). Manual fire alarm call points should be mounted in conspicuous positions on exit routes, on staircase landings, and at final exits. Items such as coat racks, potted plants etc. should not be allowed to obscure the presence of a call point, or to hinder easy access to it. |  |  |  |  |  |  |  |  |  |

3 Based on visual inspection of readily accessible areas, with a degree of sampling where appropriate.

4 A full investigation of the design of HVAC systems is outside the scope of this fire risk assessment.

5 Based on visual inspection, but no test of illuminance levels or verification of full compliance with relevant British Standards carried out.

6 Based on visual inspection, but no audibility tests or verification of full compliance with relevant British Standard carried out.

| 22. | MANUAL FIRE EXTINGUISHING APPLIANCES |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 22.1 | Reasonable provision of portable fire extinguishers? | Yes |  | No |  |
| 22.2 | Hose reels provided? | Yes |  | No |  |
| 22.3 | Are all fire extinguishing appliances readily accessible? | Yes |  | No |  |
|  | Comments and deficiencies observed: |  |  |  |  |
|  | Placed on a dedicated stand or hung on a wall at a convenient height so that employees can easily lift them off. |  |  |  |  |
| 23. | RELEVANT 7 AUTOMATIC FIRE EXTINGUISHING SYSTEMS |  |  |  |  |
| 23.1 | Type of system: |  |  |  |  |
|  | None installed. |  |  |  |  |
|  | Comments: |  |  |  |  |
| 24 | OTHER RELEVANT 7 FIXED SYSTEMS AND EQUIPMENT |  |  |  |  |
| 24.1 | Type of fixed system: |  |  |  |  |
|  | - Staircase smoke vents. - Basement smoke vents. - Two dry rising mains. |  |  |  |  |
|  | Comments: |  |  |  |  |
| 24.2 | Suitable provision of fire-fighters switch(es) for high voltage luminous tube signs, etc. | Yes |  | No |  |
|  | Comments: |  |  |  |  |
|  | None installed. |  |  |  |  |

7 Relevant to life safety and this risk assessment (as opposed purely to property protection).

MANAGEMENT OF FIRE SAFETY

| 25. | PROCEDURES AND ARRANGEMENTS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 25.1 | Fire safety is managed by:8 |  |  |  |  |  |  |
|  | The Responsible Person (name here) |  |  |  |  |  |  |
| 25.2 | Competent person(s) appointed to assist in undertaking the preventive and protective measures (i.e. relevant general fire precautions)? |  |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | MB Health & Safety Ltd. |  |  |  |  |  |  |
| 25.3 | Is there a suitable record of the fire safety arrangements? | N/A |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | - Fire safety records (i.e. Fire Log book, illustrated fire plan) are maintained to assist in managing the fire safety strategy of the premises and to demonstrate how the organisation complies with fire safety law. - ‘Annual Fire Management Schedule’ specifies the frequency of maintenance and inspection regimes, fire drills, staff training, fire risk assessment review. - The company ‘Health & Safety Policy’ document contains management arrangements that detail how the company intends to meet its regulatory obligations. |  |  |  |  |  |  |
| 25.4 | Appropriate fire procedures in place? |  |  |  |  |  |  |
|  | More specifically: |  |  |  |  |  |  |
|  | Are procedures in the event of fire appropriate and properly documented? | N/A |  | Yes |  | No |  |
|  | Are there suitable arrangements for summoning the fire and rescue services? | N/A |  | Yes |  | No |  |
|  | Are there suitable arrangements to meet the fire and rescue service on arrival and provide relevant information, including that relating to hazards to fire-fighters? | N/A |  | Yes |  | No |  |
|  | Are there suitable arrangements for ensuring that the premises have been evacuated? | N/A |  | Yes |  | No |  |
|  | Is there a suitable fire assembly point(s)? | N/A |  | Yes |  | No |  |
|  | Are there adequate procedures for evacuation of any disabled people who are likely to be present? | N/A |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | - Fire instructions notices (‘Fire action’) are displayed on escape routes adjacent to fire break-glass call points and where staff frequently assemble in the premises, e.g. the ‘break-out’ area. - The emergency plan is evaluated to determine its effectiveness and to confirm understanding of the training given, and, to provide helpful information for future training. |  |  |  |  |  |  |

8 This is not intended to represent a legal interpretation of responsibility, but merely reflects the managerial arrangement in place at the time of this risk assessment.

| 25.5 | Persons nominated and trained to use fire extinguishing appliances? | N/A |  | Yes |  | No |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Comments: |  |  |  |  |  |  |
|  | - Nominated staff trained in the use of fire extinguishers. - People with no training should not be expected to attempt to extinguish a fire. However, all staff should be familiar with the location and basic operating procedures for the equipment provided, in case they need to use it. |  |  |  |  |  |  |
| 25.6 | Persons nominated and trained to assist with evacuation, including evacuation of disabled people? | N/A |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | No disabled occupants identified at the time of this assessment. |  |  |  |  |  |  |
| 25.7 | Appropriate liaison with fire and rescue service (e.g. by fire and rescue service crews visiting for familiarisation visits)? | N/A |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | Familiarisation visits are carried out at the discretion of the fire and rescue service. No visit within the last 12 months. |  |  |  |  |  |  |
| 25.8 | Routine in-house inspections of fire precautions (e.g. in the course of health and safety inspections)? | N/A |  | Yes |  | No |  |
|  | Comments |  |  |  |  |  |  |
|  | Documented weekly and monthly site checks. |  |  |  |  |  |  |

| 26. | TRAINING AND DRILLS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 26.1 | Are all staff given adequate fire safety instruction and training on induction? |  |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | Conducted in-house. |  |  |  |  |  |  |
| 26.2 | Are all staff given adequate periodic “refresher training” at suitable intervals? |  |  | Yes |  | No |  |
|  | Comments - Conducted in-house - No formal refresher training programme is in place. However, it is anticipated that periodic fire evacuation drills will provide confirmation of the procedure to follow in the event of a fire emergency. |  |  |  |  |  |  |
| 26.3 | Does all staff training provided information, instruction or training on the following: |  |  |  |  |  |  |
|  | Fire risks in the premises? |  |  | Yes |  | No |  |
|  | The fire safety measures in the building? |  |  | Yes |  | No |  |
|  | Action in the event of fire? |  |  | Yes |  | No |  |
|  | Action on hearing the fire alarm signal? |  |  | Yes |  | No |  |
|  | Method of operation of manual call points? |  |  | Yes |  | No |  |
|  | Location and use of fire extinguishers |  |  | Yes |  | No |  |
|  | Means for summoning the fire and rescue service? |  |  | Yes |  | No |  |
|  | Identity of persons nominated to assist with evacuation? |  |  | Yes |  | No |  |
|  | Identity of persons nominated to use fire extinguishing appliances? |  |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | Basic verbal instruction is provided during a company induction process. |  |  |  |  |  |  |
| 26.4 | Are staff with special responsibilities (e.g. fire wardens) given additional training? |  |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | Nominated staff trained as fire wardens. |  |  |  |  |  |  |
| 26.5 | Are fire drills carried out at appropriate intervals? |  |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | - Records indicate these are carried out every 4 months. - No record of any fire evacuation drills documented. It is recommended that the RP conduct evacuation drills on a six monthly/annual basis and record the results in a fire log book. |  |  |  |  |  |  |
| 26.6 | When the employees of another employer work in the premises: |  |  |  |  |  |  |
|  | Is their employer given appropriate information (e.g. on fire risks and general fire precautions)? | N/A |  | Yes |  | No |  |
|  | Is it ensured that the employees are provided with adequate instructions and information? | N/A |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | - Regular sub-contractors/self-employed persons are required to sign the ‘Sub-Contractors/Self-Employed Code of Conduct’. - All visitors/contractors are required to sign-in to a register. These are closely monitored by management. |  |  |  |  |  |  |
| 27. | TESTING AND MAINTENANCE |  |  |  |  |  |  |
| 27.1 | Adequate maintenance of premises? |  |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | - A number of formal service agreements are in place. However, there is a need for further arrangements to be implemented. - The premises appeared in good visual condition. |  |  |  |  |  |  |
| 27.2 | Weekly testing and periodic servicing of fire detection and alarm system? |  |  | Yes |  | No |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |
|  | - The system is maintained under contract, on a quarterly basis. - No fire alarm test records were made available for inspection. The fire alarm should be tested weekly in accordance with the requirements of BS 5839 and the results recorded within a fire log book. - Additionally, the fire alarm system should be inspected and serviced on a six monthly basis by a competent person with specialist knowledge of fire-warning and automatic detection systems. |  |  |  |  |  |  |
| 27.3 | Monthly and annual testing routines for emergency escape lighting? |  |  | Yes |  | No |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |
|  | - No emergency lighting inspection or test records were made available for inspection. A representative of the RP should conduct a monthly visual check and a monthly ‘Flick’ test in accordance with the requirements of BS 5266 and the results recorded within a fire log book. - Additionally, the emergency lighting installation should be serviced and subjected to a three hour discharge test on an annual basis by a competent contractor. |  |  |  |  |  |  |

| 27.4 | Annual maintenance of fire extinguishing appliances? |  |  | Yes |  | No |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Comments and deficiencies |  |  |  |  |  |  |
|  | Annual service agreement in place – last undertaken Month 20** (servicing company name here) |  |  |  |  |  |  |
| 27.5 | Periodic inspection of external escape staircases and gangways? | N/A |  | Yes |  | No |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |
|  | - None installed. - Documented monthly site checks. - All employees are aware of the need for good housekeeping throughout the premises/site. This ensures that all access routes, walkways and general floor areas are kept free from obvious obstructions and potential trip hazards. |  |  |  |  |  |  |
| 27.6 | Six-monthly inspection and annual testing of rising mains? | N/A |  | Yes |  | No |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |
| 27.7 | Weekly and monthly testing, six monthly inspection and annual testing of fire-fighting lifts? | N/A |  | Yes |  | No |  |
|  | Comments and deficiencies observed: |  |  |  |  |  |  |
|  | None installed. |  |  |  |  |  |  |
| 27.8 | Weekly testing and periodic inspection of sprinkler installations? | N/A |  | Yes |  | No |  |
|  | Comments: |  |  |  |  |  |  |
|  | None installed. |  |  |  |  |  |  |

| 27.9 | Routine checks of final exit doors and/or security fastenings? | Yes |  | No |  |
| --- | --- | --- | --- | --- | --- |
|  | Comments: |  |  |  |  |
|  | - End of day ‘locking up’ procedures. - No in-house fire safety inspection regime identified at the time of this assessment. |  |  |  |  |

| 27.10 |  | Annual inspection and test of lightning protection system? | N/A |  |  | Yes |  |  | No |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Comments: |  |  |  |  |  |  |  |  |
|  |  | None installed. |  |  |  |  |  |  |  |  |
| 27.11 |  | Other relevant inspections or tests? |  |  |  | Yes |  |  | No |  |
|  |  | Comments: |  |  |  |  |  |  |  |  |
|  |  | None. |  |  |  |  |  |  |  |  |
| 28. | RECORDS |  |  |  |  |  |  |  |  |  |
| 28.1 | Appropriate records of: |  |  |  |  |  |  |  |  |  |
|  | Fire drills? |  | N/A |  |  | Yes |  |  | No |  |
|  | Fire training? |  |  |  | Yes |  |  |  | No |  |
|  | Fire alarm tests? |  | N/A |  | Yes |  |  |  | No |  |
|  | Emergency escape lighting tests? |  | N/A |  | Yes |  |  |  | No |  |
|  | Maintenance and testing of other fire protection systems? |  | N/A |  | Yes |  |  |  | No |  |
|  | Comments: |  |  |  |  |  |  |  |  |  |
|  | - Fire safety records (i.e. Fire log book, illustrated fire plan) are maintained to assist in managing the fire safety strategy of the premises and to demonstrate how the organisation complies with fire safety law. - The Fire log book is kept within the clients demise and is available for inspection by any relevant authority. |  |  |  |  |  |  |  |  |  |

FIRE RISK ASSESSMENT

The following simple risk level estimator is based on a more general health and safety risk level estimator of the type contained in BS 8800:

| Potential consequences of fire Likelihood of fire | Slight harm | Moderate harm | Extreme harm |
| --- | --- | --- | --- |
| Low | Trivial risk | Tolerable risk | Moderate risk |
| Medium | Tolerable risk | Moderate risk | Substantial risk |
| High | Moderate risk | Substantial risk | Intolerable risk |

Taking into account the fire prevention measures observed at the time of this risk assessment, it is considered that the hazard from fire (likelihood of fire) at these premises is:

| Low |  | Medium |  | High |  |
| --- | --- | --- | --- | --- | --- |

In this context, a definition of the above terms is as follows:

| Low: | Unusually low likelihood of fire as a result of negligible potential sources of ignition. |
| --- | --- |
| Medium: | Normal fire hazards (e.g. potential ignition sources) for this type of occupancy, with fire hazards generally subject to appropriate controls (other than minor shortcomings). |
| High: | Lack of adequate controls applied to one or more significant fire hazards, such as to result in significant increase in likelihood of fire. |

Taking into account the nature of the building and the occupants, as well as the fire protection and procedural arrangements observed at the time of this fire risk assessment, it is considered that the consequences for life safety in the event of fire would be:

| Slight harm |  | Moderate harm |  | Extreme harm |  |
| --- | --- | --- | --- | --- | --- |

In this context, a definition of the above terms is as follows:

| Slight harm: | Outbreak of fire unlikely to result in serious injury or death of any occupant (other than an occupant sleeping in a room in which a fire occurs). |
| --- | --- |
| Moderate harm: | Outbreak of fire could foreseeably result in injury (including serious injury) of one or more occupants, but it is unlikely to involve multiple fatalities. |
| Extreme harm: | Significant potential for serious injury or death of one or more occupants. |

Accordingly, it is considered that the risk to life from fire at these premises is:

| Trivial |  | Tolerable |  | Moderate |  | Substantial |  | Intolerable |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Comments:

A suitable risk-based control plan should involve effort and urgency that is proportional to risk. The following risk-based control plan is based on one advocated by BS 8800 for general health and safety risks:

| Risk level | Action and timescale |
| --- | --- |
| Trivial | No action is required and no detailed records need be kept. |
| Tolerable | No major additional controls required. However, there might be a need for improvements that involve minor or limited cost. |
| Moderate | It is essential that efforts are made to reduce the risk. Risk reduction measures should be implemented within a defined time period. Where moderate risk is associated with consequences that constitute extreme harm, further assessment might be required to establish more precisely the likelihood of harm as a basis for determining the priority for improved control measures. |
| Substantial | Considerable resources might have to be allocated to reduce the risk. If the building is unoccupied, it should not be occupied until the risk has been reduced. If the building is occupied, urgent action should be taken. |
| Intolerable | Building (or relevant area) should not be occupied until the risk is reduced. |

(Note that, although the purpose of this section is to place the fire risk in context, the above approach to fire risk assessment is subjective and for guidance only. All hazards and deficiencies identified in this report should be addressed by implementing all recommendations contained in the following action plan. The fire risk assessment should be reviewed regularly).

ACTION PLAN

It is considered that the following recommendations should be implemented in order to reduce fire risk to, or maintain it at, the following level:

| Trivial |  | Tolerable |  |
| --- | --- | --- | --- |

Definition of priorities (where applicable):

| Low: | Consideration should be given as to whether risks can be lowered; where applicable to a trivial level within 6-9 months |
| --- | --- |
| Medium: | Additional controls can be implemented at relatively low cost (in terms of time, money, and effort) and should be implemented as soon as possible but within 3 months maximum. |
| High: | Risks unacceptable and require immediate remedial action to reduce risk to tolerable level, or activity needs to be suspended (timescale - 1 month maximum) |

| Actions arising from assessment | Priority (where applicable) | Action by whom | Date action taken |
| --- | --- | --- | --- |
| - (7.2) All fixed electrical installations within the premises should be inspected every 5 years in accordance with Electricity at Work Regulations / IET Wiring Regulations 18th Edition / British Standard 7671. |  | Company name |  |
| - (7.2) The company should make provision for the re-inspection of portable electrical appliances in accordance with current legislation. |  | Company name |  |
| - (8.1) Suitable no smoking signage (a minimum of A5 in area) must be displayed in a prominent position at every entrance to smoke free premises. |  | Company name |  |
| - (10.3) All fixed heating installations to be serviced regularly by a competent person in accordance with manufacturer’s recommendations. |  | Company name |  |
| - (17.2) The stairs directly between the main production area and kitchen are not very clear and could easily become a trip hazard in poor visibility conditions (i.e. smoke fill, reduced lighting due to power failure etc.) Recommend that the nosing be painted white to make the stair edge obvious. |  | Company name |  |
| - (18.1) Fire resisting doors should be kept closed at all times to limit fire spread and development. |  | Company name |  |
| - (18.2, 27.11) There are a number of dampers fitted in air ducting which passes between fire resisting compartments. These all needs to be made subject to regular inspection and maintenance in accordance with the recommendations of BS9999. All work to be completed by a competent person. |  | Company name |  |
| - (20.1) - Fire instructions notices (‘Fire action’) should be displayed on escape routes adjacent to fire break-glass call points, where staff frequently assemble in the premises, e.g. the ‘break-out’ area. - Suitable signage should be displayed immediately above ‘thumb turn’ locks (fitted to final exit doors) which indicates the direction of turn to release the lock to open the door. - A notice with the words ‘Fire escape – keep clear’ should be permanently displayed at about eye level on the external face of all doors which are provided as a means of escape in case of fire and which, because they are not normally used, may become obstructed. |  | Company name |  |
| - (25.3, 25.4) Appropriate fire procedures/emergency plan must be developed and communicated to staff and others (i.e. clients/contractors) that could be affected in the event of a fire emergency. |  | Company name |  |
| - (25.5, 25.6, 26.1, 26.2, 26.3) Adequate fire safety information, instruction, and training must be provided to all staff as soon as possible after they are appointed and regularly after that. Your training should include the following: - what to do on discovering a fire; - how to raise the alarm and what happens then; - what to do upon hearing the fire alarm; - the procedures for alerting contractors and visitors including, where appropriate, directing them to exits; - the arrangements for calling the fire and rescue service; - the evacuation procedures for everyone on site to reach an assembly point at a place of total safety; - the location and, when appropriate, the use of firefighting equipment; - the location of escape routes, especially those not in regular use; - how to open all emergency exit doors; - the importance of keeping fire doors closed to prevent the spread of fire, heat and smoke; - where appropriate, how to stop machines and processes and isolate power supplies in the event of a fire; - the reason for not using lifts (except those specifically installed or nominated, following a suitable fire risk assessment); - the safe use of and risks from storing or working with highly flammable and explosive substances; and - the importance of general fire safety, which includes good housekeeping. |  | Company name |  |
| - (26.4) Those expected to undertake a supervisory role (i.e. Fire Marshals) if there is a fire should receive additional training, this may include: - detailed knowledge of the fire safety strategy of the premises; - awareness of human behaviour in fires; - how to encourage others to use the most appropriate escape route; - how to search safely and recognise areas that are unsafe to enter; - the difficulties that some people, particularly if disabled, may have in escaping and any special evacuation arrangements that have been pre-planned; - additional training in the use of firefighting equipment; - an understanding of the purpose of any fixed firefighting equipment such as sprinklers or gas flooding systems; and - reporting of faults, incidents and near misses. |  | Company name |  |
| - (26.5) The emergency plan must be evaluated to determine its effectiveness. The best way to do this is to perform a fire drill. This should be carried out at least annually. A well-planned and executed fire drill will confirm understanding of the training given, and provide helpful information for future training. |  | Company name |  |
| - (27.2) The fire alarm system to be tested weekly at a pre-determined time using a different call point for each successive test to check that the sounders operate satisfactorily. |  | Company name |  |
| - (27.3) A maintenance and testing regime must be implemented for the installed emergency escape lighting system(s). Typically, this would include: - a monthly function test by operating the test facility for a period sufficient to ensure that each emergency lamp illuminates; and - an annual full discharge test. |  | Company name |  |
| - (27.4) Maintenance of portable fire extinguishing appliances by a competent person should be carried out annually. |  | Company name |  |
| - (25.8, 28.1) Fire safety records (i.e. Fire Log book, illustrated fire plan) must be maintained to assist in managing the fire safety strategy of the premises and to demonstrate how the organisation complies with fire safety law. |  | Company name |  |
| - It is recommended that the Responsible Person review the fire risk assessment regularly (recommended every 12 months), so as to keep it up to date and particularly if there have been significant changes in the matters to which it relates, i.e. the premises, technical and/or organisational measures, or, failures relating to the existing fire safety precautions. | 12 months from date of this assessment | Responsible Person |  |

APPENDIX 1 - PHOTOS

| Blocked escape route | Blocked escape route/pallets stored against building |
| --- | --- |
| Fire Exit sign obscured by blinds | Incomplete Fire Action Notice |
| Fire Extinguishers blocked | Fire Log Book not completed |