Fire Risk Assessment Review

Regulatory Reform (Fire Safety) Order 2005

| Responsible Person |  | EnTrust Global Ltd |  |  |
| --- | --- | --- | --- | --- |
| Address of Premises |  | 5th floor, 30 Panton Street, London |  |  |
| Postcode |  | SW1Y 4AJ |  |  |
| Original Assessor: |  | Philippa Parker |  |  |
| Date of Original Fire Risk Assessment |  | 7th September 2022 |  |  |
| (This risk assessment should be reviewed annually or at such earlier time as there is reason to suspect that it is no longer valid or there has been a significant change in the matters to which it relates.) |  |  |  |  |
| Subsequent Review Dates |  |  |  |  |
| Reviewed by | Tony Smith-Allen (MBHS Ltd) |  | Date | 7th Sept 2022 |
| Reviewed by | Tony Smith-Allen (MBHS Ltd) |  |  | 26th March 2024 |

General Information

| The Premises |  |
| --- | --- |
| Number of floors in demise: | 1 (5th) |
| Approximate floor area: (m²) | 524.9 m2 |
| Primary usage: | Office |

| Occupancy Profile |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum number of persons in the most highly occupied compartment to be affected by an uncontrolled fire within 30 minutes, assuming no evacuation. | WEEKDAYS |  |  | WEEKENDS |  |  |  |  |
|  | 0000 to 0400 |  | A | 0000 to 0400 |  |  | A |  |
|  | 0400 to 0800 |  | A | 0400 to 0800 |  |  | A |  |
|  | 0800 to 1200 |  | B | 0800 to 1200 |  |  | A |  |
|  | 1200 to 1600 |  | B | 1200 to 1600 |  |  | A |  |
|  | 1600 to 2000 |  | B | 1600 to 2000 |  |  | A |  |
|  | 2000 to 2400 |  | A | 2000 to 2400 |  |  | A |  |
|  | Range – A= <20, B=20-49, C=50-99, D=100-1000, E=>1000, 0= None |  |  |  |  |  |  |  |
| Description of Occupants | Mobility Issues | A | Average Mobility |  | B | Vulnerability Issues |  | A |

| Occupants Especially at Risk from Fire |  |
| --- | --- |
| Disabled occupants (Personal Emergency Evacuation Plans in use when necessary) | 0 |
| Occupants in remote areas (Lone working/isolated areas) | 0 |
| Young persons (Individual Risk Assessment provided for those persons under 16 yrs) | 0 |
| Others (Details of Elderly/Infirm/Mental Ability) | Pregnant employees periodically |
| Visitors | A |
| Occupants whose first language is not English | A |

Identified Fire Hazards And Primary Control Measures

| Smoking |  |  |  |  |
| --- | --- | --- | --- | --- |
| Measures taken to prevent fires as a result of smoking. |  |  |  |  |
| Smoking prohibited in the building? |  |  |  | YES |
| Smoking permitted in appropriate areas? |  |  |  | NO |
| Suitable arrangements for those who wish to smoke? |  |  |  | NO |
| Identified Hazards | Existing Control Measures |  | Are there any improvement recommendations |  |
| Smoking in building | No smoking or vaping in the building | No |  |  |

| Arson/Deliberate Ignition |  |  |  |
| --- | --- | --- | --- |
| Basic security against arson by outsiders or other persons appears reasonable. |  |  | YES |
| Is there the potential for fire load/combustibles in close proximity to the premises available for ignition by outsiders? |  |  | NO |
| Identified Hazards | Existing Control Measures | Are there any improvement recommendations |  |
| 1. Security | The building management has 24-hour security and CCTV. Reception is staffed and manage all visitors etc | No |  |

| Fixed Heating Installations |  |  |  |
| --- | --- | --- | --- |
| Fixed heating installations such as boilers are used within the premises. |  |  | YES |
| Are fixed heating installations subject to regular maintenance? |  |  | YES |
| Are suitable measures taken to minimise the hazard of ignition of combustible materials due to these heaters? |  |  | YES |
| Identified Hazards | Existing Control Measures | Are there any improvement recommendations |  |
| 1. Hot water heaters | Housed within their own cupboards and away from combustible materials. | No |  |

| Portable Heaters |  |  |  |
| --- | --- | --- | --- |
| Portable heaters are used within the premises. |  |  | NO |
| Is the use of the more hazardous type (i.e. radiant bar fires or LPG appliances) avoided? |  |  | YES |
| Are suitable measures taken to minimise the hazard of ignition of combustible materials due to these heaters? |  |  | YES |
| Identified Hazards | Existing Control Measures | Are there any improvement recommendations |  |
| None |  |  |  |
| General Comments: The building heating system currently appears to be efficient enough to circulate air movements to a level that means supplementary heaters are unlikely to be required. However, this will be kept under review as the colder months are approaching and a more accurate view can be taken. |  |  |  |

| Electrical Sources of Ignition |  |  |  |  |
| --- | --- | --- | --- | --- |
| Measures taken to prevent fires of electrical origin. |  |  |  |  |
| Fixed installation periodically inspected and tested? (every 5 years) |  |  |  | YES |
| Portable appliance testing carried out on a risk assessed basis? |  |  |  | YES |
| Suitable policy in place regarding the use of personal electrical appliances? |  |  |  | YES |
| Suitable limitation and management of trailing leads and adaptors? |  |  |  | YES |
| Identified Hazards | Existing Control Measures |  | Are there any improvement recommendations |  |
| 1. Fixed installation 2. PAT 3. Personal equipment 4. Trailing leads | Checked every 5 years. Checked annually. Discouraged, only phone chargers. Kept in cable trays. |  | No No No No |  |
| Deficiencies: None |  | Remedial Action Required: None |  |  |

| Cooking |  |
| --- | --- |
| Measures taken to prevent fires as a result of cooking. |  |
| Filters cleaned or changed and ductwork cleaned regularly? | N/A |
| Suitable extinguishing appliances available? (e.g. Fire blanket, Wet Chemical etc) | N/A |
| Suitable Shut Down Procedures in place? | N/A |
| General Comments: No cooking facilities, only microwaves |  |

| Lightning |  |  |  |
| --- | --- | --- | --- |
| The building has a lightning protection system. |  |  | YES |
| Is the lightning protection system subject to a suitable maintenance regime? |  |  | YES |
| Identified Hazards | Existing Control Measures | Are there any improvement recommendations |  |
| Lightening protection system | The building management team complete external inspections. Copies could be available on request if required. |  |  |

| Dangerous Substances |  |
| --- | --- |
| Dangerous substances are, or could be used or stored, within the premises? | N/A |
| A risk assessment has been carried out as required by the Dangerous Substances and Explosive Atmospheres Regulations 2002? | N/A |
| Stored in suitable areas and containers away from potential sources of ignition, to include issues of chemical reactivity and compatibility. | N/A |

| Housekeeping |  |
| --- | --- |
| Standards of housekeeping. |  |
| Combustible materials appear to be separated from ignition sources? | YES |
| Appropriate storage of hazardous materials? | N/A |
| Escape routes kept clear of any combustibles. | YES |
| Appropriate measures for the safe storage and disposal of waste? | YES |

| Hazards Introduced by Contractors and Building Works |  |
| --- | --- |
| Fire safety conditions have been imposed on both external contractors and in-house maintenance staff? | YES |
| Is there satisfactory control over works including use of hot work permits, where appropriate, carried out in the building by external contractors? Details: Complete risk assessment done for Building Manager before works start | YES |
| If there are in-house maintenance personnel, are suitable precautions taken during works carried out by them, including use of hot work permits, where appropriate? Details: Building Management complete risk assessments | YES |
| Other Significant Fire Hazards That Warrant Consideration |  |
| Are there any other fire hazards that warrant consideration within the premises? | NO |

Arrangements for Evacuation

| Evacuation Strategy |  |
| --- | --- |
| Typical evacuation strategies within the premises are likely to involve one or more of the following arrangements. |  |
| Single Stage Evacuation It is reasonably expected that all relevant persons in the premises are able to (and will) evacuate immediately to a place of total safety. | YES |
| Progressive Horizontal Evacuation Relevant persons are dependant on staff to assist with their escape. Provisions have been made to move such persons from an area affected by fire, through a fire resisting barrier to an adjoining fire protected area on the same level, where they can wait in a place of safety whilst the fire is dealt with or await further evacuation down a protected route to total safety. | NO |

Provision of Elements of Fire Safety as Secondary Control Measures

| Means of Escape |  |  |  |
| --- | --- | --- | --- |
| It is considered that the premises are provided with reasonable means of escape in case of fire. ( See plan at end) |  |  | YES |
| Adequate design of escape routes? |  |  | YES |
| Reasonable distances of travel when: |  |  |  |
| Where there is escape in a single direction? State the distance of .maximum travel. |  |  | 10 metres max |
| Where there are alternative means of escape? State the distance of maximum travel. |  |  | 10 metres max |
| Suitable protection of escape routes? (Fire resisting construction) |  |  | YES |
| Adequate provision of exits? |  |  | YES |
| Exits easily and immediately open-able where necessary without the use of a key? |  |  | YES |
| Escape routes unobstructed? |  |  | YES |
| It is considered that the premises are provided with reasonable arrangements for means of escape for disabled people? Describe the arrangements below. |  |  | YES |
| Does the evacuation plan fit with the floor space factors? |  |  | YES |
| Identify dead end corridors. Are the appropriately covered? |  |  | N/A |
| Identify inner rooms. Are the appropriately covered? |  |  | YES |
| Identified Hazards | Existing Control Measures | Are there any improvement recommendations |  |
| Disabled escape | Evacuation chair and dedicated staff to use it | No |  |
| Emergency escape | Multiple routes of escape that are within distance of travel (45m) as depicted in Table 2 of HM Gov Guide on Fire Risk Assessment in Offices and Shops | No |  |

| Measures to Limit Fire Spread and Development |  |
| --- | --- |
| It is considered that there is: |  |
| Compartmentation of a reasonable standard. (Fire resisting) | YES |
| Reasonable limitation of linings that may promote fire spread. | YES |
| As far as can be reasonable ascertained, fire dampers are provided in ducts or vents as necessary to protect critical means of escape routes against passage of fire, smoke and combustion products in the early stages of a fire? | YES |

| Emergency Escape Lighting |  |  |  |  |
| --- | --- | --- | --- | --- |
| It is considered that there is a reasonable standard of emergency escape lighting to ensure safe use of escape routes |  |  |  | YES |
| Identified Hazards | Existing Control Measures |  | Are there any improvement recommendations |  |
| None | Emergency lighting noted along escape routes and above emergency exit doors. |  |  |  |
| Deficiencies: None |  | Remedial Action Required: None |  |  |

| Fire Safety Signs and Notices |  |  |  |  |
| --- | --- | --- | --- | --- |
| It is considered that there is a reasonable standard of fire safety signs and notices? This to include fire exit, fire resisting door and hazard signage. The signage should comply to Health & Safety (Signs and signals) Regulations BS1996 |  |  |  | YES |
| Identified Hazards | Existing Control Measures |  | Are there any improvement recommendations |  |
| None | Directional signs, Fire Action Notices and Extinguisher content signage in place providing a good level of information to the occupants. |  |  |  |
| Deficiencies: None |  | Remedial Action Required: |  |  |

| Means of Giving Warning In Case Of Fire |  |
| --- | --- |
| Reasonable manually operated fire warning system provided? | YES |
| If yes give details: Break glass call points |  |
| Automatic fire detection provided? | YES |
| Throughout Premises | YES |
| Extent of automatic fire detection generally appropriate for the occupancy and fire risk? | YES |
| Remote transmission of alarm signals to a monitoring station or other? | YES |

| Manual Fire Extinguishing Appliances |  |
| --- | --- |
| Reasonable provision of portable fire extinguishers? | YES |
| Are all fire extinguishing appliances readily accessible and unobstructed? | YES |
| Is suitable wall signage provided relevant to extinguisher? | YES |
| Are hose reels provided? | NO |

| Relevant Automatic Fire Extinguishing Systems |  |
| --- | --- |
| Type of fixed system and location | N/A |

Management of Fire Safety

| Procedures and Arrangements |  |  |
| --- | --- | --- |
| Fire safety is managed by: | Building management for whole building, Entrust Global - Janice Shepherd for floor 5 |  |
| Deputy or assistant: | None |  |
| Are competent person(s) appointed to assist in undertaking the preventative and protective measures (i.e. relevant general fire precautions)? |  | YES |
| Is there a suitable record of the fire safety arrangements? |  | YES |
| Appropriate fire procedures in place? |  | YES |
| Are procedures in the event of a fire appropriate and properly documented? |  | YES |
| Are there suitable arrangements for summoning the Fire and Rescue Service? |  | YES |
| Are there suitable arrangements to meet the F&RS on arrival and provide relevant information, including that relating to hazards to fire fighters? |  | YES |
| Is there a plan of the building available indicating basic layout and any areas of significant risk? |  | YES |
| Are there suitable arrangements for ensuring that the premises have been evacuated? |  | YES |
| Is there a suitable fire assembly point(s)? |  | YES |
| Are there adequate procedures for evacuation of any disabled people who are likely to be present? |  | YES |
| Persons nominated and trained to assist with evacuation, Including evacuation of disabled people? |  | YES |
| Appropriate liaison (if necessary) with Fire and Rescue Service crews visiting for familiarisation visits? |  | YES |
| Routine in-house inspections of fire precautions (e.g. in the course of health and safety inspections)? |  | YES |

| Training and Drills |  |  |
| --- | --- | --- |
| Fire safety training is managed by: | Building Management on behalf of the Landlord |  |
| Deputy or assistant: | Security guards |  |
| Are all staff given adequate fire safety instruction and training on induction? |  | YES |
| Are all staff given adequate periodic ‘refresher’ training at suitable intervals? If yes, at what intervals? – Bi-annually |  | YES |
| Are all staff with special responsibilities (e.g. fire wardens and staff who assist with disabled people) given additional training? |  | YES |
| Are fire drills carried out at appropriate intervals and a record of such drills maintained? |  | YES |
| Are there sufficient and adequate channels of communication of fire safety information between employer and employee (e.g. Health & Safety meetings, notice boards etc) |  | YES |
| When the employees of another employer work in the premises, are they provided with adequate instructions and given appropriate information (e.g. on fire risks and fire safety measures)? |  | YES |
| Is there adequate co-operation and co-ordination between different Responsible Persons (Multi-Occupancy) to ensure compliance with the Fire Safety Order? |  | N/A |

| Testing and Maintenance |  |  |
| --- | --- | --- |
| Testing and Maintenance is managed by: | Building Manager |  |
| Deputy or assistant: | Site Engineer |  |
| Adequate maintenance of workplace? |  | YES |
| Weekly testing and periodic servicing of fire detection and alarm system to include ancillary equipment (e.g. door hold open devices, door locks etc) |  | YES |
| Monthly and annual testing routines for emergency escape lighting? |  | YES |
| Annual maintenance of fire extinguishing appliances? |  | YES |
| Periodic inspection of external escape staircases and gangways? |  | YES |
| Six monthly inspection and annual testing of rising mains? |  | N/A |
| Weekly and monthly testing, six monthly inspection and annual testing of fire fighting lifts? |  | N/A |
| Weekly testing and periodic inspection of sprinkler installations? |  | N/A |
| Routine checks of final exit doors and/or security fastenings? |  | YES |
| Annual inspection and testing of lightning protection system? |  | YES |

| Recording |  |
| --- | --- |
| Appropriate records held for: |  |
| Fire drills? | YES |
| Fire training? | YES |
| Fire alarm tests? | YES |
| Emergency escape lighting tests? | YES |
| Maintenance and testing of other fire precaution systems? | N/A |
| Location of Records: (Available for inspection by Fire Authority if required) | YES |

| Significant Findings – Remedy Action Plan |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No | Action to be Taken | Priority | Target Completion Date | Action by | Date Action Completed |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |

Fire evacuation plan:

5th Floor: